## Sheet1
| iec_category_id | iec_acronym | iec_category_name | iec_level | iec_category_description | priority | category_source | iec_category_business_name | iec_category_business_description | contractual_category_id | business_macro_category | iec_level_four_id | edart_graph_color | na_iec_category_key | gads_group | major_event_category_id | curtailment_category | curtailment_event_category | scheduled | created_by | creation_date | modified_by | modification_date
0 | 100000002 | IUud | Unclassified Downtime | 5 | The WTG is Non-Operative and the alarm code has not been auto-allocated. The downtime must be re-allocated to the correct category. | 999 | EDF Renewables | Unclassified Downtime | \N | 2 | Unclassified Downtime | 2 | ffffff | 18 | FTH | 1 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
1 | 2 | IU | Information Unavailable | 1 | The WTG information is unavailable in the database. | 998 | IEC TS 61400-26-1:2011 | Information Unavailable | \N | 2 | Information Unavailable. | \N | ffffff | 124 | FTH | 10 | \N | \N | \N | maurc | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
2 | 301 | IAFM | Force Majeure | 4 | The WTG is Non-Operative due to damage attributed to a Force Majeure events. That damage WTG Collection System Substation. (Lightning strikes storm damage acts of god) | 900 | IEC TS 61400-26-1:2011 | Force Majeure | \N | 2 | Others | 301 | 0 | 17 | RUTH | 8 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
3 | 12040201 | IANOSa | Suspended Authorities | 5 | The WTG is Non-Operative following a request from the authorities to stop an operation on site or stop a turbine resulting in energy loss. | 812 | EDF Renewables | Suspended Authorities | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
4 | 11040201 | IANOSmp | Suspended Manpower | 5 | The WTG is Non-Operative due to a lack of manpower to perform the Unscheduled Maintenance. | 811 | EDF Renewables | Suspended Manpower | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
5 | 10040201 | IANOSlmc | Suspended Logistics Major Component | 5 | The WTG is Non-Operative due to a Major Component that is not available in the inventory. | 810 | EDF Renewables | Suspended Logistics MCR | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 9 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
6 | 9040201 | IANOSlpc | Suspended Logistics 3rd Party Contractor | 5 | The WTG is Non-Operative due to waiting for a 3rd party contractor to perform the Unscheduled Maintenance | 809 | EDF Renewables | Suspended Logistics 3P | \N | 1 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
7 | 8040201 | IANOSlbop | Suspended Logistics BoP | 5 | The WTG is Non-Operative due to a BOP Spare Part that is not available in the inventory. | 808 | EDF Renewables | Suspended Logistics BoP | \N | 2 | BOP | 40201 | 67001e | \N | FTH | 2 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
8 | 7040201 | IANOSen | Suspended Engineering | 5 | The WTG is Non-Operative due to awaiting engineer recommendation for corrective actions. | 807 | EDF Renewables | Suspended Engineering | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
9 | 6040201 | IANOSe | Suspended WTG Access | 5 | The WTG is Non-Operative and corrective actions cannot be performed due to WTG access being prevented by site roads being snow drifted deferred road maintenance county road restrictions (frost laws and transportation permits delays). | 806 | EDF Renewables | Suspended Enviro | \N | 2 | Technical | 40201 | 67001e | 1017 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
10 | 5040201 | IANOSoem | Suspended WTG OEM Delay | 5 | The WTG is Non-Operative due to delayed OEM support required through an agreement between such OEM and the Owner when EDF is providing O&M on the WTGs. | 805 | EDF Renewables | Suspended OEM | \N | 2 | Technical | 40201 | 67001e | 1009 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
11 | 4040201 | IANOSo | Suspended Response | 5 | The WTG is Non-Operative due to damage fault failure or alarm which has disabled components or systems due to a Serial Loss. | 804 | EDF Renewables | Suspended Response | \N | 2 | Technical | 40201 | 67001e | 1008 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
12 | 3040201 | IANOSs | Suspended Safety Stand Down | 5 | The WTG is Non-Operative and corrective actions are prevented due to conditions that are outside the EDF-RS safety policy for performing Services or due to conditions that prevent EDF-RS from accessing the necessary portions of the Plant. Examples: high winds icing/ice throw shutdown lightning air quality active flooding recent flooding damage roads being unsafe to travel personnel. | 803 | EDF Renewables | Suspended Safety | \N | 2 | Technical | 40201 | 67001e | 1007 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
13 | 2040201 | IANOSd | Suspended Serial Defect or Loss | 5 | The WTG is Non-Operative due to delays in receiving Owner approval required to purchase Plant Components or perform reimbursable work. | 802 | EDF Renewables | Suspended Serial Defect | \N | 2 | Technical | 40201 | 67001e | 1006 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
14 | 1040201 | IANOSl | Suspended Logistics | 5 | The WTG is Non-Operative due to a Plant Component that is not available in the inventory or while awaiting a crane or hoist to perform Major Component Unscheduled Maintenance up to the point where the crane or hoist is hook ready. | 801 | EDF Renewables | Suspended Logistics | \N | 2 | Technical | 40201 | 67001e | 1005 | FTH | 8 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
15 | 40201 | IANOS | Suspended | 4 | N/A (do not use) | 800 | IEC TS 61400-26-1:2011 | Suspended | \N | 2 | Technical | 40201 | 67001e | 186 | FTH | 8 | \N | \N | 0 | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
16 | 2030201 | IANOFOmc | Forced Outage Major Component | 5 | The WTG is Out of Service due to a Major Component failure and the replacement. | 702 | EDF Renewables | Forced Outage MCR | \N | 1 | Technical | 30201 | a40025 | \N | FTH | 9 | \N | \N | 0 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
17 | 1030201 | IANOFObop | Forced Outage BoP | 5 | The WTG is Out of Service due to electrical parameters outside of the WTG OEM specifications due to a BOP Electrical Outage. (do not use for Grid events) | 701 | EDF Renewables | Forced Outage BoP | \N | 2 | BOP | 30201 | 8c0251 | 13 | FTH | 2 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
18 | 30201 | IANOFO | Forced Outage | 4 | The WTG is Non-Operative due to an active fault alarm logged in the WTG status. | 700 | IEC TS 61400-26-1:2011 | Forced Outage | \N | 1 | Technical | 30201 | a40025 | 7 | FTH | 6 | \N | \N | 0 | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
19 | 4020201 | IANOPCAmc | Planned Corrective Action Major Component | 5 | The WTG is Non-Operative due to a Major Component replacement or repair. | 604 | EDF Renewables | Planned Corr Action MCR | \N | 1 | Technical | 20201 | 313596 | \N | FTH | 9 | \N | \N | 1 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
20 | 3020201 | IANOPCAbop | Planned Corrective Action BoP | 5 | The WTG is Non-Operative due to BOP Unscheduled Maintenance. | 603 | EDF Renewables | Planned Corr Action BoP | \N | 2 | BOP | 20201 | 8c0251 | \N | FTH | 2 | \N | \N | 1 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
21 | 2020201 | IANOPCAd | Planned Corrective Action Existing Defect | 5 | The WTG is Non-Operative due to an Existing Defect. Typically defects identified during after End of Contract or Warranty Inspections. | 602 | EDF Renewables | Planned Corr Action Serial Defect | \N | 2 | Technical | 20201 | 313596 | 1001 | FTH | 7 | \N | \N | 1 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
22 | 1020201 | IANOPCAr | Planned Corrective Action Retrofit or Upgrade | 5 | The WTG is Non-Operative due to Owner-requested Reimbursable Services/Expenses to retain restore or improve the intended functional life of the WTG. Example: install fire suppression equipment condition base monitoring equipment Vortex Generator auto-lubrication equipment etc. | 601 | EDF Renewables | Planned Corr Action Retrofit/Upgrade | \N | 2 | Technical | 20201 | 313596 | 1002 | FTH | 7 | \N | \N | 1 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
23 | 20201 | IANOPCA | Planned Corrective Action | 4 | The WTG is Non-Operative due to EDF-RS Unscheduled Maintenance. | 600 | IEC TS 61400-26-1:2011 | Planned Corr Action | \N | 1 | Technical | 20201 | 313596 | 9 | FTH | 7 | \N | \N | 1 | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
24 | 1010201 | IANOSMbop | Scheduled Maintenance BoP | 5 | The WTG is Non-Operative due to BOP Scheduled Maintenance as required by the O&M Procedures Manual(s). | 501 | EDF Renewables | Scheduled Maintenance BoP | \N | 2 | BOP | 10201 | 8c0251 | \N | FTH | 2 | \N | \N | 1 | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
25 | 10201 | IANOSM | Scheduled Maintenance | 4 | The WTG is Non-Operative due to Scheduled Maintenance as required by the O&M Procedures Manual(s). | 500 | IEC TS 61400-26-1:2011 | Sched Maintenance | \N | 1 | Technical | 10201 | 4575b3 | 8 | MTH | 7 | \N | \N | 1 | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
26 | 104020101 | IAONGELg | Out of Electrical Specification Grid | 5 | The WTG is Out of Service due to electrical parameters outside of the WTG OEM specifications due to a Grid Outage. | 401 | EDF Renewables | Out of Elec Grid | \N | 2 | BOP | 4020101 | 8c0251 | 1014 | FTH | 3 | \N | \N | \N | maurc | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
27 | 4020101 | IAONGEL | Out of Electrical Specification | 4 | The WTGS is operative but not generating as the electrical conditions at the WTGS terminals are outside design specifications ( voltage. Frequency. phase imbalance) | 400 | IEC TS 61400-26-1:2011 | Out of Elec | \N | 2 | BOP | 4020101 | 8c0251 | \N | FTH | 2 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
28 | 1403020101 | IAONGRSwu | Requested Shutdown Wildlife Unplanned | 5 | The WTGS is operative but stopped by an external request due to unexpected wildlife protection compliance. | 318 | EDF Renewables | Req Shutdown Wildlife Unplanned | \N | 2 | Environmental | 3020101 | 7f643d | \N | RUTH | 6 | wildlife | C1 | \N | AELX | 2021-10-28 14:00:00 | RTC | 2023-05-31 11:30:00
29 | 1103020101 | IAONGRSsl | Requested Shutdown Structural Load | 5 | The WTG is Out of Service because the turbine is at risk of collapsing. | 317 | EDF Renewables | Req Shutdown Structure Load | \N | 2 | Others | 3020101 | 4b005c | \N | PTH | 2 | \N | \N | \N | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
30 | 1303020101 | IAONGRSeco | Requested Shutdown Economic | 5 | The WTG is Out of Service due to negative electricity pricing. | 316 | EDF Renewables | Req Shutdown Economic | \N | 2 | Others | 3020101 | 4b005c | \N | RSTH | 2 | \N | \N | \N | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
31 | 1203020101 | IAONGRSlm | Requested Shutdown Load Management | 5 | The WTG is Out of Service for load control purposes. | 315 | EDF Renewables | Req Shutdown Load Manage | \N | 2 | Environmental | 3020101 | c489ff | \N | PTH | 2 | load_management | C1 | \N | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
32 | 1003020101 | IAONGRSe | Requested Shutdown Environmental | 5 | The WTGS is operative but stopped by an external request due to extreme environmental conditions expected | 314 | IEC TS 61400-26-3:2016 ANNEX F | Req Shutdown Enviro | \N | 2 | Environmental | 3020101 | c489ff | \N | RUTH | 2 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
33 | 903020101 | IAONGRSoem | Requested Shutdown OEM | 5 | The WTG is Non-Operative due to OEM performing services on the WTG required through an agreement between such OEM and the Owner. | 313 | EDF Renewables | Req Shutdown OEM | \N | 1 | Technical | 3020101 | 4b005c | 1010 | PTH | 7 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
34 | 803020101 | IAONGRSo | Requested Shutdown Owner | 5 | The WTG is Out of Service due to an Owner-requested shut down to perform Site Tours Audits or RCAs. | 312 | EDF Renewables | Req Shutdown Owner | \N | 2 | Others | 3020101 | 4b005c | 1004 | PTH | 7 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
35 | 703020101 | IAONGRSg | Requested Shutdown Grid | 5 | The WTG is Out of Service due to receiving an external curtailment due to Plant output directives from QSE the transmission provider or the regional transmission authority or if the EDF-RS initiates shutdowns due to the Plant not responding to the output directive. | 311 | IEC TS 61400-26-3:2016 ANNEX F | Req Shutdown Grid | \N | 2 | BOP | 3020101 | c41d79 | 12 | RSTH | 3 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
36 | 603020101 | IAONGRSem | Requested Shutdown Emergency | 5 | The WTG is Out of Service due to an emergency situation at the Plant. | 310 | EDF Renewables | Req Shutdown Emergency | \N | 2 | Others | 3020101 | 4b005c | 1003 | PTH | 7 | \N | \N | 0 | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
37 | 503020101 | IAONGRSnu | Requested Shutdown Noise Unplanned | 5 | The WTGS is operative but stopped by an external request due to unexpected acoustic noise compliance | 309 | EDF Renewables | Req Shutdown Noise Unplanned | \N | 2 | Environmental | 3020101 | 4b005c | \N | RUTH | 6 | noise | C1 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
38 | 403020101 | IAONGRSn | Requested Shutdown Noise | 5 | The WTGS is operative but stopped by an external request due to acoustic noise compliance | 308 | IEC TS 61400-26-3:2016 ANNEX F | Req Shutdown Noise | \N | 2 | Environmental | 3020101 | c489ff | \N | RUTH | 2 | noise | C1 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
39 | 303020101 | IAONGRSwb | Requested Shutdown Wildlife Bat | 5 | The WTG is Out of Service due to an active warning code for a bat protection protocol. | 307 | EDF Renewables | Req Shutdown Bat | \N | 2 | Environmental | 3020101 | 7f643d | \N | RUTH | 2 | wildlife | C1 | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
40 | 203020101 | IAONGRSw | Requested Shutdown Wildlife | 5 | The WTG is Out of Service due to an active warning code for a wildlife protection protocol. | 306 | IEC TS 61400-26-3:2016 ANNEX F | Req Shutdown Wildlife | \N | 2 | Environmental | 3020101 | 7f643d | 1015 | RUTH | 2 | wildlife | C1 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
41 | 103020101 | IAONGRSf | Requested Shutdown Flicker | 5 | The category FLICKER is obtained when the WPS or WTGS is operative but not functioning as it has been stopped by an external request due to visual flicker compliance. | 305 | IEC TS 61400-26-3:2016 ANNEX F | Req Shutdown Flicker | \N | 2 | Environmental | 3020101 | c489ff | \N | RUTH | 2 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
42 | 3020101 | IAONGRS | Requested Shutdown | 4 | The WTG is Out of Service due to the shutdown initiated by the EDF-RS. | 300 | IEC TS 61400-26-1:2011 | Req Shutdown | \N | 2 | Others | 3020101 | 4b005c | 11 | PTH | 7 | \N | \N | 0 | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
43 | 402020101 | IAONGENct | Out of Environmental Specification Cold Temperature or Icing | 5 | The WTG is Out of Service due to an active warning code for cold weather or icing event. | 206 | EDF Renewables | Out of Enviro Icing / Low Temp | \N | 2 | Environmental | 2020101 | 34988f | 123 | RUTH | 4 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
44 | 302020101 | IAONGENht | Out of Environmental Specification High Temperature | 5 | The WTG is Out of Service due to an active warning code for high temperatures outside of WTG OEM specifications or Plant specific requirements. | 205 | EDF Renewables | Out of Enviro High Temp | \N | 2 | Environmental | 2020101 | 34988f | 14 | RUTH | 4 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
45 | 202020101 | IAONGENhw | Out of Environmental Specification High Winds | 5 | The WTG is Out of Service due to wind speeds above WTG OEM specifications. | 202 | IEC TS 61400-26-3:2016 ANNEX F | Out of Enviro High Winds | \N | 4 | Environmental | 2020101 | 34988f | 16 | RUTH | 4 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
46 | 102020101 | IAONGENcw | Out of Environmental Specification Calm Winds | 5 | The WTG is Out of Service due to wind speeds below WTG OEM specifications. | 201 | IEC TS 61400-26-3:2016 ANNEX F | Out of Enviro Calm Winds | \N | 4 | Environmental | 2020101 | a9d08e | 15 | RUTH | 11 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
47 | 2020101 | IAONGEN | Out of Environmental Specification | 4 | the WTG is operative but not functioning as the conditions of the environment are out of the design specifications. | 200 | IEC TS 61400-26-1:2011 | Out of Enviro | \N | 2 | Environmental | 2020101 | 34988f | \N | RUTH | 4 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
48 | 1020101 | IAONGTS | Technical Standby | 4 | The WTG is Out of Service due to the performance of autonomous tasks required for maintaining intended functions. Example: yaw untwisting battery test brake test heat up | 100 | IEC TS 61400-26-1:2011 | Technical Standby | \N | 2 | Technical | 1020101 | a9d08e | 10 | RUTH | 5 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
49 | 3010101 | IAOSRS | Ready Standby | 4 | The WPS is in the category READY STANDBY when ready to respond to a predefined event. | 90 | IEC TS 61400-26-3:2016 | Ready Standby | \N | 4 | Environmental | 3010101 | a9d08e | \N | RUTH | 11 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
50 | 1102010101 | IAOGPPdrlm | Partial Performance Derated Load Management | 5 | The WTG is Operating at a reduced performance for load control purposes. | 36 | EDF Renewables | Partial Perf Load Manage | \N | 2 | Environmental | 2010101 | 7ecec1 | \N | CTH | 12 | load_management | C2 | \N | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
51 | 1002010101 | IAOGPPdra | Partial Performance Derated Authorities | 5 | The WTG is Operating at a reduced performance upon request of the Authorities. | 35 | EDF Renewables | Partial Perf Authorities | \N | 2 | Others | 2010101 | 7ecec1 | \N | CTH | 12 | \N | \N | \N | AELX | 2021-06-24 16:00:00 | RTC | 2023-05-31 11:30:00
52 | 902010101 | IAOGPPdgi | Partial Performance Degraded Icing | 5 | The WTG is Operating at reduced performance compared to the predefined power curve for reasons attributed to Icing. | 34 | EDF Renewables | Partial Perf Degraded Icing | \N | 2 | Environmental | 2010101 | b6dbfe | 1013 | CTH | 12 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
53 | 702010101 | IAOGPPdrg | Partial Performance Derated Grid | 5 | The WTG is Operating at reduced performance due to partial external curtailment due to Plant output directives from QSE the transmission provider the regional transmission authority or other Party. | 33 | IEC TS 61400-26-3:2016 ANNEX F | Partial Perf Grid | \N | 2 | BOP | 2010101 | c41d79 | 4 | CTH | 12 | \N | \N | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
54 | 602010101 | IAOGPPdri | Partial Performance Derated Cold Temperature or Icing | 5 | The WTG is Operating at reduced performance due to an active warning code for cold temperature or icing that makes the WTG unable to operate at Full Performance per design specifications. | 32 | EDF Renewables | Partial Perf Icing / Low Temp | \N | 2 | Environmental | 2010101 | b6dbfe | 5 | CTH | 12 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
55 | 502010101 | IAOGPPdrt | Partial Performance Derated High Temperature | 5 | The WTG is Operating at reduced performance due to an active warning code due to high temperatures outside the WTG OEM specifications or Plant specific requirements. | 31 | EDF Renewables | Partial Perf High Temp | \N | 2 | Environmental | 2010101 | b6dbfe | 1012 | CTH | 12 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
56 | 402010101 | IAOGPPdnu | Partial Performance Derated Noise Unplanned | 5 | The WTG is Operating at reduced performance due to unexpected noise compliance curtailments. | 30 | EDF Renewables | Partial Perf Noise Unplanned | \N | 1 | Technical | 2010101 | c489ff | 1016 | CTH | 12 | noise | C2 | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
57 | 302010101 | IAOGPPdrn | Partial Performance Derated Noise Planned | 5 | The performance is limited by expected curtailments due to noise compliance | 29 | IEC TS 61400-26-3:2016 ANNEX F | Partial Perf Noise | \N | 2 | Environmental | 2010101 | c489ff | \N | CTH | 12 | noise | C2 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
58 | 202010101 | IAOGPPdrm | Partial Performance Derated Manual | 5 | The WTG is Operating at reduced performance due to a decision to either not run at Full Performance due to safety concerns or to extend the functional life of a Plant Component. | 28 | EDF Renewables | Partial Perf Manual | \N | 2 | Others | 2010101 | 7ecec1 | 1000 | CTH | 12 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
59 | 102010101 | IAOGPPdr | Partial Performance Derated | 5 | The WTG is Operating at reduced performance due to an active warning code caused by a defective part or uncalibrated part. | 23 | EDF Renewables | Partial Perf Derated | \N | 2 | Others | 2010101 | 7ecec1 | 3 | CTH | 12 | \N | C3 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
60 | 802010101 | IAOGPPdg | Partial Performance Degraded | 5 | The WTG is Operating at reduced performance compared to the predefined power curve for reasons not attributed to any of the following Partial Performances: Derate Derate High Temperature Derate Cold Temperature or Icing Derate Manual Grid Derate Noise Planned or Degraded Icing. | 22 | EDF Renewables | Partial Perf Degraded | \N | 1 | Technical | 2010101 | fbb963 | 2 | CTH | 12 | \N | C3 | \N | maurc | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
61 | 2010101 | IAOGPP | Partial Performance | 4 | The WTGS is operative and generating with technical restrictions or other limitations which affect generation. | 20 | IEC TS 61400-26-1:2011 | Partial Perf | \N | 2 | Others | 2010101 | fbb963 | \N | CTH | 12 | \N | C3 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
62 | 101010101 | IAOGFPw | Full Performance Active Warning | 5 | The WTG is Operating according to design specifications with an active warning. | 11 | IEC TS 61400-26-3:2016 ANNEX F | Full Perf Warning | \N | 4 | \N | 1010101 | 83bb5d | 6 | CTH | 11 | \N | C3 | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
63 | 1010101 | IAOGFP | Full Performance | 4 | The WTG is operative and functioning according to design specifications with no technical restrictions or limitations beyond the ones specified in the design specifications. | 10 | IEC TS 61400-26-1:2011 | Full Perf | \N | 4 | \N | 1010101 | 83bb5d | 1 | CTH | 11 | \N | C3 | \N | AELX | 2019-02-20 00:00:00 | RTC | 2023-05-31 11:30:00
64 | 20101 | IAONG | Information Available Operative Non-Generating | 3 | The WTGS is operative but not generating because one of the underlying information categories is active. | 5 | IEC TS 61400-26-1:2011 | Non-Generating | \N | 2 | Others | \N | ffffff | \N | FTH | 1 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
65 | 10101 | IAOG | Information Available Operative Generating | 3 | The WTGS is converting wind energy into electrical energy and or providing reactive compensation. | 4 | IEC TS 61400-26-1:2011 | Generating | \N | 4 | \N | \N | ffffff | \N | CTH | 10 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
66 | 201 | IANO | Information Available Non-Operative | 2 | The WTGS is not capable of performing the generation functions. | 3 | IEC TS 61400-26-1:2011 | Non-Operative | \N | 1 | Others | \N | ffffff | \N | FTH | 1 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
67 | 101 | IAO | Information Available Operative | 2 | The WTGS is capable of performing the intended functions. regardless of whether it is actually active and regardless of the capacity level that can be provided. | 2 | IEC TS 61400-26-1:2011 | Operative | \N | 4 | \N | \N | ffffff | \N | CTH | 10 | \N | \N | \N | AELX | 2019-08-09 00:00:00 | RTC | 2023-05-31 11:30:00
68 | 1 | IA | Information Available | 1 | All time periods. during which information on the WPS and external conditions is retrieved. logged and stored manually or automatically to the extent that at least one information category can be established. | 1 | IEC TS 61400-26-1:2011 | Information Available | \N | \N | \N | \N | ffffff | \N | FTH | 10 | \N | \N | \N | AELX | 2019-09-24 16:00:00 | RTC | 2023-05-31 11:30:00
69 | 1202010101 | IAOGPPdrbop | Partial Performance Derated BOP | 5 | The WTG is operating at reduced performance due to substation derate caused by damaged Balance of Plant equipment. | 37 | EDF Renewables | Partial Perf Derated BOP | \N | 2 | BOP | 2010101 | c489ff | \N | CTH | 12 | \N | \N | \N | RTC | 2023-05-30 17:00:00 | RTC | 2023-05-31 11:30:00
70 | 14040201 | IANOSlca | Suspended Logistics Commercial Availability | 5 | The WTG is non operative due to parts not being commercially available per the O&m contractual definition. | 814 | EDF Renewables | Suspended Logistics Commercial | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | RTC | 2023-05-30 17:00:00 | RTC | 2023-05-31 11:30:00
71 | 13040201 | IANOSro | Suspended Response Owner | 5 | The WTG is suspended waiting the response from owner. This category added because default suspended response is considered UMC for PBA Management.This category will be configured as OMC. | 813 | EDF Renewables | Suspended Response Owner | \N | 2 | Technical | 40201 | 67001e | \N | FTH | 8 | \N | \N | 0 | RTC | 2023-05-30 17:00:00 | RTC | 2023-05-31 11:30:00